# Transformer Thermal and Degradation Modeling Plan

This document outlines the strategy for integrating transformer thermal constraints and insulation degradation. The models are based on industry standards IEEE C57.91 (Thermal Dynamics) and incorporate harmonic loss adjustments per IEEE C57.110.

## 1. Thermal Dynamics (IEEE C57.91)

The thermal model tracks how electrical load (K) and ambient temperature (ΘA) affect the transformer's top-oil and winding hot-spot temperatures over time.

### Top-Oil Temperature Dynamics

The top-oil temperature responds slowly to load changes due to high thermal mass. Its dynamics are governed by a first-order differential equation:

τTOdΔΘTOdt=ΔΘTO,U-ΔΘTO

The ultimate top-oil temperature rise (ΔΘTO,U) for a given load step is:

ΔΘTO,U=ΔΘTO,RK2R+1R+1n

Integration Note: To account for harmonic currents from data center equipment, the Harmonic Loss Factor (FHL) from IEEE C57.110 should be multiplied by K2 to capture additional resistive heating.

### Winding Hot-Spot Temperature Dynamics

The winding hot-spot is the critical metric for insulation degradation. It reacts much faster than the oil temperature.

τHdΔΘHdt=ΔΘH,U-ΔΘH

The ultimate hot-spot temperature rise (ΔΘH,U) over the top-oil for a given load is:

ΔΘH,U=ΔΘH,RK2m

### Total Absolute Temperatures

To calculate absolute temperatures used for the degradation model and constraints:

Absolute Top-Oil Temperature:ΘTO=ΘA+ΔΘTO

Absolute Hot-Spot Temperature:ΘH=ΘTO+ΔΘH

## 2. Transformer Degradation and Loss of Life (LoL)

Degradation of the transformer's paper insulation is evaluated using the Arrhenius equation. This calculates how much faster the insulation ages when the hot-spot temperature exceeds the 110°C baseline.

### Aging Acceleration Factor (FAA)

For standard thermally upgraded paper, the aging rate is calculated as:

FAA=exp15000383-15000ΘH+273

### Calculating Loss of Life

To find the cumulative degradation over the scheduling horizon, integrate the Aging Acceleration Factor over time. The Equivalent Aging (in hours) for a time horizon is:

LEQ=t=1NFAA,t×Δt

Expressed as a Percent Loss of Life (% LoL):

%LoL=LEQ180,000×100

(Assuming a standard normal insulation life of 180,000 hours).